## Sheet1
SRP Sustainability Guidelines Checklist
Project Name:
Checklist Issue Date:
1.0 Sustainable Principles
SP1.1 Daylighting: Natural light has health and productivity benefits to office staff and should be evaluated on all projects. The amount of light needs to be balanced with the associated heat gain.
Measure | Yes | No | N/A | Discussion | Remarks
Daylight Model |  |  |  | For new construction, the project should provide a daylighting model that is coordinated with the energy model to create a final design solution. These models should account for glazing properties (SHGC, VLT, U Value) and interior and exterior shading devices.
Window Replacement Options |  |  |  | For existing buildings, examine windows and shading devices. Provide options to SRP for consideration including the following high priority components: install new internal window shades, replace single pane glazing with dual pane, install low-e coated or other high-performance glazing. Team should provide estimated annual energy savings with these upgrades as part of energy study in section 2.
Window Shades
SP1.2 Sustainable Site: Incorporate strategies in the design of the project site that will create a more sustainable project. Project team to consider credits from LEED and Green Globes and present to SRP project team with cost benefit analysis for each item and then incorporate those features as directed by SRP. The following topics should be considered for inclusion on all projects.
Measure | Yes | No | N/A | Discussion | Remarks
Bicycle Facilities |  |  |  | Bicycle Facilities. Provide code minimum bike storage per local jurisdiction’s zoning regulations and add as needed specifically for that site’s usage. Provide employee showers where it makes sense, quantity to be discussed with SRP for final decision. Applicable to certain sites – SRP will add additional bike storage racks in response to local demand on each site.
Heat Island Mitigation |  |  |  | Heat Island Mitigation. Select paving and roof materials with appropriate SRI vales. Add landscaping to site that will provide shade at hardscape surfaces.
Carpool / HOV / FEV Parking |  |  |  | Provide carpool designated spaces on all projects. Refer to SRP Transportation group for quantity. Provide electric charging infrastructure at each facility for these vehicles.
Site Lighting Controls |  |  |  | Site lighting controls to have dusk-to-dawn timers at a minimum but may include additional controls based on SRP use on a project specific case. Site lighting should also limit uplight and trespass beyond the property lines. Site lighting should always consider safety as primary factor.
SP1.3 Site Water Management:
Measure | Yes | No | N/A | Discussion | Remarks
Stormwater Runoff to Planters |  |  |  | Stormwater harvesting is not required on projects. Water runoff from roof and hardscape areas should be retained on site and directed to planter areas where possible. Always comply with local jurisdiction requirements for water management.
Condensate Water Recovery |  |  |  | Condensate water recovery should be considered on projects with central dehumidification or DOAS units. Where projects would only gain value from condensate collection during monsoon, this should not be implemented except as part of a larger water recovery plan.
SP1.4 Enhanced Building Commissioning:
Measure | Yes | No | N/A | Discussion | Remarks
Commissioning Plan |  |  |  | The following systems and associated controls, where included in the building project, should be commissioned:
a. Heating, ventilating, air-conditioning, and refrigeration systems and associated controls. b. Air-curtain systems. c. Lighting systems: automatic and manual daylighting controls, occupancy sensing devices, automatic shut-off controls, time switching, and other lighting control devices, and dimming systems d. Domestic hot-water systems and controls. e. Water pumping and mixing systems over and purification systems. f. Irrigation system performance. g. Renewable energy systems and energy storage systems. h. Energy and building management and demand-control systems.
Post Occupancy Cx |  |  |  | The Cx plan should contain postoccupancy Cx requirements in accordance with ANSI/ASHRAE/ IES Standard 202. The Cx provider should provide the owner with a complete systems manual, all record documents, and a complete final Cx report in accordance with Standard 202.
2.0 Energy Performance
EP2.1 IECC Compliance: All new buildings should perform better than the current IECC energy code requirements. Existing buildings being modified should perform better on elements of the project that are being altered.
Measure | Yes | No | N/A | Discussion | Remarks
Meet Perscriptive Requirements |  |  |  | Investigate buildings energy performance by either exceeding prescriptive energy requirements or by completing an energy model that shows the building exceeds the performance of the base building.
Complete Energy Model
Enhanced envelope performance. |  |  |  | Investigate which High Efficiency Options under C406 of the IECC may be applicable for this buidling.
Reduced lighting power.
More efficient HVAC equipment
EP2.2 Energy Metering:
Measure | Yes | No | N/A | Discussion | Remarks
HVAC Sub-Meter |  |  |  | Energy distribution systems should be designed such that each primary circuit, panel, feeder, piping system or supply mechanism supplies only one energy use category. Adequate space should be provided for installation of metering equipment or other data collection devices, temporary or permanent, to measure their energy use. The meter data should be mapped into the BAS where practical.
People Moving Sub-Meter
Lighting Sub-Meter
Plug/process Loads Sub-Meter
Solar Sub-Meter
EP2.3 Renewable Energy: For new buildings, conduct a study to determine the technical feasibility and life-cycle cost effectiveness of on-site renewable energy.
Measure | Yes | No | N/A | Discussion | Remarks
Provide Life-cycle Cost Analysis |  |  |  | Each new building or site should be equipped with onsite renewable energy systems in accordance with the following: Provide not less than 2.0 kWh per square foot of roof Area for single story or not less than 3.0 kWh per square foot of roof Area for multiple story. When PV is deemed not cost feasible, the project should set aside “solar ready” areas that would meet the above criteria.
Provide Solar Panels
Make Building Solar Ready
EP2.4 Auto Demand Response:
Measure | Yes | No | N/A | Discussion | Remarks
Provide DR Infrastructure |  |  |  | Building projects should contain automatic control systems that have the capability to reduce building equipment loads to lower electric peak demand of the building. The building controls should be designed with automated demand-response (DR) infrastructure capable of receiving DR requests from the utility, electrical system operator, or third-party DR program provider and automatically implementing load adjustments to the HVAC and lighting systems.
3.0 Water Conservation
WC3.1 Indoor Water Use:
Measure | Yes | No | N/A | Discussion | Remarks
All Fixtures Meet EPA 1992 |  |  |  | Make sure the project fixtures comply with EPA 1992 law.
Investigate High Eff. Fixtures |  |  |  | Investigate high efficient fixtures for this project.
WC3.2 Water Metering:
Measure | Yes | No | N/A | Discussion | Remarks
Water Source Sub-Meter |  |  |  | Water consumed from any source associated with the building or building site should be metered separately. Each meter should be able to communicate water consumption data remotely and provide daily data reporting capability that can produce reports that show daily, monthly, and annual water consumption. Meter data should be mapped into the BAS where practical.
Water Use Sub-Meters |  |  |  | All water supplied to the applications listed below should be individually metered. Similar appliances and equipment should be permitted to be grouped & supplied from piping connected to a single meter. • Cooling Towers • Evaporative coolers • Steam and Hot Water Boilers • Irrigation • Separate buildings • Large Process
WC3.3 Outdoor Water Use:
Measure | Yes | No | N/A | Discussion | Remarks
Plant Selection |  |  |  | Ensure new plants comply with SRP Design Guidelines and Specifications. Investigate the replacement of existing plants with those that meet the SRP Standard Specifications.
Irrigation |  |  |  | Ensure new irrigation systems comply with SRP Design Guidelines and Specifications. Investigate the replacement of the existing irrigation system with one that meets the SRP Standard Specifications.
`
WC3.4Process Water:
Measure | Yes | No | N/A | Discussion | Remarks
Process Water Investigation |  |  |  | Evaluate the proposed uses of process water by the building occupants and building systems. The project team should evaluate alternative means and methods to reduce the usage of single pass domestic water for process water usages that are not mission critical.